[image: image1.jpg]TWO
RIVERS

WISCONSIN



Two Rivers City Hall
1717 East Park Street
Two Rivers, WI 54241
(920) 793-5532 www.two-rivers.org

CITY OF TWO RIVERS CITY COUNCIL

PUBLIC UTILITIES COMMITTEE
Tuesday, December 7, 2021 - 6:00 P.M. 
City Hall – Third Floor, COUNCIL CHAMBERS

MINUTES
Call to Order






Roll Call – Committee Members: Bonnie Shimulunas, Jay Remiker, Bill LeClair (virtually)
Staff Present: Jim Mc Donald (Public Works Director), Scott Ahl (Civil Engineer II), Dave Casebeer (Wastewater Utility), Ross Blaha (Water Utility), Brian Delleman (Electric Utility)
Guest:  Greg Droessler, Town & Country Engineering
      Review and Approval of Minutes – Motion was made by Jay Remiker, seconded by Bonnie Shimulunas, to approve the minutes as presented. Motion carried with unanimous voice vote.
Review of Current Projects:


Pine Tree Lift Station – hope to begin or complete substantially in January

Eggers (290th St) Pond - soil management approval to haul soils off site
CWF and SDWLP projects for 2022 include:

WWTP Screw Press – Pilot tested 5 different units (no cost to City)
· Received 6 proposals (one vendor submitted 2 different units)

· Analyzed proposals based on capital costs, operational cost (including polymer)

· Sites visited:  PW Tech – only produced sludge with 18% solids; Schwing – squeegees only lasted 2 years (should have lasted 7 years); FKC – 23% solids, lower plymer usage, low maintenance, seemed well built, could last longer

· Based on analysis, recommend FKC with conveyor but without control panel: designed for 1000#/hr.yr (close to existing press); currently designed for operation 3 days/wk.  Recommended control panel to be designed and supplied through contract to ensure compatibility with plant SCADA system.
· Noted selected system will be included in package for bidding early 2022.
Motion made by Jay Remiker, seconded by Bonnie Shimulunas, to recommend the FKC screw press to City Council for approval
Electric Utility:  
· Pine Tree Lift Station: set new pole
· Finishing 2021 project (11th St, Hawthorne to Columbus)

· MJ Electric working to inspect poles and wiring along river crossing between 31st & Parkway to Columbus & Hawthorne

· Tree trimming letters were sent to east side residents
Water Utility:  
· Reservoir considered a deficiency on sanitary survey; overflow is out of code per DNR; need to design and construct new overflow
· DNR requesting using orthophosphates to reduce lead lateral issues; city consultant/scientist suggests a pilot study on high pressure zone as they do not feel the changes required

Set Date, Time, Location and Agenda Items for next Committee Meeting
   Next Meeting will be held Tuesday, January 4, 2022, at 600 pm.
Adjournment – Motion by Jay Remiker, seconded by Bonnie Shimulunas, to adjourn at 6:33pm 
